# Electrical Equipment Inspection & Testing PROCEDURE

### Introduction

This procedure provides direction and information for PCBU’s, workers and contractors regarding the testing of electrical equipment on ${legalname} owned and operated worksites. It aims to ensure the integrity of electrical appliances in worksites and the safety of personnel who use it.

Scope

This procedure applies to equipment owned by ${legalname}, workers and contractors.

This procedure does not apply to:

- electrical equipment at a height of 2.5m or greater above the ground, floor or platform;

- equipment which would need to be dismantled to perform the inspection and tests;

- fixed or stationary electrical equipment that forms part of the electrical installation and falls within the scope of AS3000:2000 Electrical Installations (known as the AUS/NZ Wiring Rules).

When the equipment is new, the supplier is deemed responsible for the initial electrical safety of the new equipment. New equipment need not be inspected or tested. However it must be tagged in accordance with Clause 2.4.2. AS/NZS 3760.

### Definitions

Electrical equipment includes

- portable, handheld and stationary appliances designed for connection to the low voltage supply by a flexible cord; cord extension sets and Electrical Portable Outlet Devices (EPODs) or power boards.

- flexible cords connected to fixed equipment in hostile environments

- portable isolation transformers

- Residual Current Devices (RCDs) – portable type (PRCD), socket type outlet and fixed switchboard type

- Commercial and industrial battery chargers

- Portable and transportable 415v heavy duty tools, such as high pressure cleaners and concrete grinders.

Competent person a person who has acquired through training, qualification, experience or a combination of these, the knowledge and skill enabling that person to correctly and safely perform the task of electrical testing.

Hostile Environments is an environment where the equipment or appliance is normally subjected to events or operating conditions likely to result in deterioration and or subsequent damage to equipment where electrical safety could be affected. This includes but is not limited to physical abuse, exposure to moisture, heat, vibration, corrosive chemicals and dust.

PAT Portable appliance tester

Residual current device (RCD) - A mechanical switching device designed to make, carry and break currents under normal service conditions, and to cause the opening of the contacts when the residual current attains a given value under specified conditions.

### Roles and Responsibilities

Managers/Supervisors are responsible for:

- ensuring electrical equipment and RCDs are tested and tagged in accordance with AS/NZS 3760

- ensuring test registers are maintained in accordance with this procedure

- ensuring persons carrying out electrical testing and tagging in their area of responsibility and accountability is a competent person

Workers are responsible for:

- reporting to Line Managers, electrical equipment or RCDs that have not been tested or have expired test dates

- ensuring any equipment brought into the workplace is tested and tagged prior to use

### Procedure

All electrical equipment shall be electrically tested and tagged in accordance with the procedure and at intervals specified in AS/NZS 3760 unless testing interval has been varied by the completion of a risk assessment, prior to use.

Ensure that a competent and appropriately trained person completes the electrical testing

Test and tag any privately owned electrical appliances brought onto the worksite prior to use (e.g. heaters, frypans, crock pots, kettles etc.)

Immediately remove from service and attach “danger tag” to non-compliant electrical equipment for repair or disposal. STAFF MUST NOT USE EQUIPMENT TAGGED AS FAULTY.

Hired/loaned electrical equipment

Equipment hired/loaned by (or brought onto) the site is inspected prior to hire/use and has been tested and tagged within 3 months prior to hiring/loaning. An inspection consists of a visual and tactile examination of the cord, plug and equipment to ensure their integrity, i.e. no cuts, breaks, burns or exposed wires.

Tagging

Compliant equipment shall be fitted with a tag which should identify the period in which the test was done and shall include:

- The name of the person or company who made the inspection or carried out the test or maintenance; and

- The test, inspection or maintenance date; and

- A re-test date if required

Equipment out of service

It is known that some work areas place electrical equipment out of service and place into storage (otherwise known as mothballing) as the equipment is only used seasonally or infrequently. In this case, the equipment must be fitted with an out of service tag (as per the Energy Isolation Tags and Lock Off procedure) and placed into a locked store room or similar. When the item is placed back in-service the out of service tag is to be removed and the item is only required to be retested and tagged if the test date has expired, if there is no test tag on the equipment, then it must be retested.

Contractors

Contractors shall not use electrical equipment on ${legalname} workplaces unless testing of their electrical equipment has been carried out in accordance with AS/NZS 3760.

Record Keeping

An external provider shall be required to provide a copy of all test results. Records of formal inspections, tests and repairs are to be retained for a period of not less than seven years.

Records of inspection and testing to be kept include:

- A register of all electrical equipment

- A record of formal inspection and tests

- A record of faulty equipment

### References

Work Health & Safety Act 2012 (SA)

Work Health & Safety Regulations 2012 (SA)

SafeWork Australia Managing electrical risks at the workplace – Code of Practice

AS/NZS 3760: 2010 In-service safety inspection and testing of electrical equipment.

AS/NZS 5762:2005 In-service safety inspection and testing – Repaired electrical equipment

Plumbers, Gasfitters and Electricians Act 1995.

### Forms

### Nil

Authority

Signature:

Authorised by: ${officer} 	Title: ${role}

Date: ${date}

Indicative testing and inspection intervals for electrical equipment

(This must be read in conjunction with AS/NZS 3760 as a whole and particularly 2.1)

| Type of environment and/or equipment | Interval between inspection and tests |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Equipment Including Class I, Class II equipment, cord sets, cord extension sets and EPODs | Residual Current Devices (RCD’s) |  |  |  |  |
|  |  | Push–button test – by user |  |  | Operating time and push-button test |  |
| (a) | (b) | Portable (c) | Fixed (d) | Portable (e) |  | Fixed (f) |
| 1. Factories, workshops, places of, manufacture, assembly, maintenance or fabrication | 6 months | Daily, or before every use, whichever is the longer | 6 months | 12 months |  | 12 months |
| 2. Environment where the equipment or supply flexible cord is subject to flexing in normal use OR is open to abuse OR is in hostile environment | 12 months | 3 months | 6 months | 12 months |  | 12 months |
| 3. Environment where the equipment or supply cord is NOT subject to flexing in normal use and is NOT in a hostile environment | 5 years | 3 months | 6 months | 2 years |  | 2 years |
| 4. Residential type areas of: hotels, residential institutions, motels, boarding houses, halls, hostels accommodation houses, and the like | 2 years | 6 months | 6 months | 2 years |  | 2 years |
| 5. Equipment used for commercial cleaning | 6 months | Daily, or before every use, whichever is the longer | N/A | 6 months |  | N/A |
| 6. Hire equipment; Inspection Test & tag | Prior to hire | Including push-button test by hirer prior to hire |  | N/A |  | N/A |
|  | 3 months | N/A |  | 3 months |  | 12 months |
| 7. Repaired, serviced and second hand equipment | After repair or service which could affect electrical safety, or on reintroduction to service, refer to AS/NZS 5762 |  |  |  |  |  |